# Line Disconnector

Controllable line disconnector function without interlocking support The XSWI and CSWI applies to all three phases of the switch.

The switch supports local and remote operation. The local operation mode is indicated. Health is indicated for the electrical equipment. There is an operation counter and the function provides block open and block close indication.

The switch control model requires Select Before Operate with enhanced security. It uses the services SelectWithValue, Cancel, Operate, TimeActivatedOperate, and CommandTermination. Once not in the unselected state, only the client that selected the control object is able to force state transitions for the control object.