## Sheet0
Sort Key | Substation | Short Name Substation | SSEN Voltage Level Reference | Bay Name | SSEN Bay Number | SSEN Bay Reference | Plant | Device Model | IP@ & Mask (/23=255.255.254.0 /24=255.255.255.0) | IED Role | IED Name | Indication Group | Function | Description | HMI Dataset Inclusion | TCC Dataset Inclusion | TCC DNP3 Address Required | TCC Voltage | TCC Circuit | TCC Group Name | HMI Description | Reaction Matrix | HMI Circuit Reference | Future Use | 61850 Data Type | DNP3 Data Type (Static Object) | HMI (Copadata) Data Type | 61850 Address with Functional Constraint | Full 61850 Path | DNP3 Address | DNP3 Data Type | Test Result | Added | Deleted | Changed | HMI_Variable_Element | Copadata_Symbolic_Address | HMI | HMI_1 | TCC | TCC_1
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | Backup Overcurrent Protection Disabled | X | X | X | 132kV | ULK | Backup Protection Urgent | Backup Overcurrent Protection Disabled | REM_ALM_IN_OUT_15 | ULK |  | ENUM |  | USINT | Protection/OcpPTOC2.Beh.stVal[ST] |  | 500 | 30 | [5 empty] | LIMKE01BUP!LIMKE01BUPProtection/OcpPTOC2/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Event | Backup Protection Alarms | Backup Overcurrent Protection Start | X | X |  | 132kV | ULK |  | Backup Overcurrent Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/OcpPTOC2.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPProtection/OcpPTOC2/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | Backup Overcurrent Protection Operated | X | X | X | 132kV | ULK | Backup Protection Operated | Backup Overcurrent Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/OcpPTOC2.Op.general[ST] |  | 502 | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPProtection/OcpPTOC2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | Backup Earth Fault Protection Disabled | X | X | X | 132kV | ULK | Backup Protection Urgent | Backup Earth Fault Protection Disabled | REM_ALM_IN_OUT_15 | ULK |  | ENUM |  | USINT | Protection/EfmPTOC2.Beh.stVal[ST] |  | 501 | 30 | [5 empty] | LIMKE01BUP!LIMKE01BUPProtection/EfmPTOC2/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Event | Backup Protection Alarms | Backup Earth Fault Protection Start | X | X |  | 132kV | ULK |  | Backup Earth Fault Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/EfmPTOC2.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPProtection/EfmPTOC2/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | Backup Earth Fault Protection Operated | X | X | X | 132kV | ULK | Backup Protection Operated | Backup Earth Fault Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/EfmPTOC2.Op.general[ST] |  | 503 | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPProtection/EfmPTOC2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | Backup Protection DAR Lockout | X | X | X | 132kV | ULK |  | Backup Protection DAR Lockout | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/LedGGIO1.Ind8.stVal[ST] |  | 506 | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPSystem/LedGGIO1/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | <bay.name> BCU Fail | X | X | X | 132kV | ULK | Control System Urgent | ULK BCU Fail | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind3.stVal[ST] |  | 504 | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPSystem/GosGGIO2/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Event | Backup Protection Alarms | Backup Protection Disturbance Record Available | X | X |  | 132kV | ULK |  | Backup Protection Disturbance Record Available | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | Records/RDRE1.RcdMade.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPRecords/RDRE1/RcdMade/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P141 | 192.168.248.19 /23 | P141_BUP | LIMKE01BUP | Alarm | Backup Protection Alarms | Backup Protection Clock Synchronisation Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | Backup Protection Clock Synchronisation Alarm | REM_ALM_ON_OFF | ULK |  | BOOL |  | BOOL | System/LLN0.SyncSt.stVal[ST] |  | 505 | 1 | [5 empty] | LIMKE01BUP!LIMKE01BUPSystem/LLN0/SyncSt/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC3 | X | X |  | 132kV | ULK |  | DAR Start (Protn Trip) | REM_ALM_RST_START | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind3.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC4 | X | X |  | 132kV | ULK |  | DAR Start (Inter Trip) | REM_ALM_RST_START | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC6 | X | X |  | 132kV | ULK |  | DAR Block | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC8 | X | X | X | 132kV | ULK | Control System Non Urgent | DAR Local | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind8.stVal[ST] |  | 1007 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC11 | X | X |  | 132kV | ULK |  | Spare - Slot F / Binary Input CC11 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind11.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC12 | X | X |  | 132kV | ULK |  | Spare - Slot F / Binary Input CC12 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind12.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC13 | X | X |  | 132kV | ULK |  | Spare - Slot F / Binary Input CC13 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC5 | X | X | X | 132kV | ULK | DAR Non Urgent | DAR Inhibited | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind36.stVal[ST] |  | 1070 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind36/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot F / Binary Input CC7 | X | X | X | 132kV | ULK | DAR Lockout | DAR Lockout | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind39.stVal[ST] |  | 1071 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind39/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot G / Binary Input CC4 | X | X |  | 132kV | ULK |  | Spare - Slot G / Binary Input CC4 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot G / Binary Input CC5 | X | X |  | 132kV | ULK |  | Spare - Slot G / Binary Input CC5 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot G / Binary Input CC6 | X | X |  | 132kV | ULK |  | Spare - Slot G / Binary Input CC6 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot G / Binary Input CC7 | X | X |  | 132kV | ULK |  | Spare - Slot G / Binary Input CC7 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot G / Binary Input CC8 | X | X |  | 132kV | ULK |  | Spare - Slot G / Binary Input CC8 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot H / Binary Input CC16 | X | X | X | 132kV | ULK | Control System Urgent | BCU Control Switch on Isolated | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind16.stVal[ST] |  | 1013 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot H / Binary Input CC13 | X | X |  | 132kV | ULK |  | Spare - Slot H/ Binary Input CC13 | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC1 | X | X |  | 132kV | ULK |  | Spare - Slot J / Binary Input CC1 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind1.stVal[ST] |  |  | 1 | Not Set |  |  |  |  | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC2 | X | X |  | 132kV | ULK |  | Spare - Slot J / Binary Input CC2 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind2.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC3 | X | X | X | 132kV | ULK | Control System Urgent | Common Bay BCU Backup PSU Not Ready | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind3.stVal[ST] |  | 1016 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC4 | X | X | X | 132kV | ULK | Control System Urgent | Common Bay BCU Main PSU Not Ready | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind4.stVal[ST] |  | 1017 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC5 | X | X |  | 132kV | ULK |  | Spare - Slot J / Binary Input CC5 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC6 | X | X |  | 132kV | ULK |  | Spare - Slot J / Binary Input CC6 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC7 | X | X |  | 132kV | ULK |  | Spare - Slot J / Binary Input CC7 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC8 | X | X |  | 132kV | ULK |  | Spare - Slot J / Binary Input CC8 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC9 | X | X | X | 132kV | ULK | Control System Non Urgent | First Main Protection VT MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind9.stVal[ST] |  | 1020 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC10 | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection VT MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind10.stVal[ST] |  | 1021 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC11 | X | X | X | 132kV | ULK | Control System Non Urgent | Fault Recorder VT MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind11.stVal[ST] |  | 1022 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC12 | X | X | X | 132kV | ULK | Control System Non Urgent | BCU VT MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind12.stVal[ST] |  | 1023 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC13 | X | X | X | 132kV | ULK | Control System Non Urgent | Burden Resistor VT MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind13.stVal[ST] |  | 1024 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC14 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC14 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC15 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC15 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC16 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC16 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC18 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC18 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind18.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind18/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC19 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC19 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind19.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC20 | X | X | X | 132kV | ULK | Control System Non Urgent | 105 Switchgear Heater MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind20.stVal[ST] |  | 1031 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind20/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC21 | X | X | X | 132kV | ULK | Control System Non Urgent | 105 Marshalling Kiosk Heater / Illuminiation MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind21.stVal[ST] |  | 1032 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind21/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC28 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC28 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind28.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind28/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC29 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC29 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind29.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind29/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC30 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC30 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind30.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind30/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC31 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC31 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind31.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind31/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot J / Binary Input CC32 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC32 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind32.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind32/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC1 | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection & Second Intertrip IED Defective | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind1.stVal[ST] |  | 1044 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC2 | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection & Second Intertrip DC Supply MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind2.stVal[ST] |  | 1045 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC3 | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection GPS DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind3.stVal[ST] |  | 1046 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC4 | X | X | X | 132kV | ULK | Trip Relays Operated | Second Main Protection Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind4.stVal[ST] |  | 1047 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC5 | X | X | X | 132kV | ULK | Trip Relays Operated | Second Intertrip Receive Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind5.stVal[ST] |  | 1048 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC6 | X | X | X | 132kV | ULK | Backup Protection Urgent | Backup Protection IED Defective | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind6.stVal[ST] |  | 1049 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC7 | X | X | X | 132kV | ULK | Control System Non Urgent | Backup Protection DC Supply MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind7.stVal[ST] |  | 1050 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC8 | X | X | X | 132kV | ULK | Trip Relays Operated | Backup Protection Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind8.stVal[ST] |  | 1051 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC9 | X | X |  | 132kV | ULK |  | Fault Recorder Faulty/PQM Defective | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC10 | X | X | X | 132kV | ULK | Control System Non Urgent | Fault Recorder PSU DC MCB Trip/PQM DC MCB Trip/PQ Sensor DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind10.stVal[ST] |  | 1053 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC11 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC11 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind11.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC12 | X | X | X | 132kV | ULK | Control System Non Urgent | Fault Recorder GPS Fail | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind12.stVal[ST] |  | 1055 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC13 | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection GPS Fail | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind13.stVal[ST] |  | 1056 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC14 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC14 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC15 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC15 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC16 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC16 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | Feeder Alarm | Slot 2H/ Binary Input CC17 | X | X |  | 132kV | ULK |  | Wind Farm Circuit Breaker Open | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind17.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind17/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | Feeder Alarm | Slot 2H/ Binary Input CC18 | X | X |  | 132kV | ULK |  | Wind Farm Circuit Breaker Closed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind18.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind18/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | Feeder Alarm | Slot 2H/ Binary Input CC19 | X | X |  | 132kV | ULK |  | Wind Farm Emergency Trip Operated | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind19.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | Feeder Alarm | Slot 2H/ Binary Input CC20 | X | X |  | 132kV | ULK |  | Wind Farm Protection Faulty | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind20.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind20/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC21 | X | X | X | 132kV | ULK | Control System Urgent | Emergency Trip Operated | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind21.stVal[ST] |  | 1064 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind21/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC22 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC22 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind22.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind22/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC23 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC23 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind23.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind23/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC24 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC24 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind24.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind24/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC25 | X | X | X | 132kV | ULK | Control System Urgent | Alarm Supply MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind25.stVal[ST] |  | 1066 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind25/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC26 | X | X | X | 132kV | ULK | Control System Urgent | BCU DC Supply 1 MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind26.stVal[ST] |  | 1067 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind26/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC27 | X | X | X | 132kV | ULK | Control System Urgent | BCU DC Supply 2 MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind27.stVal[ST] |  | 1075 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind27/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2H/ Binary Input CC28 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC28 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind28.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind28/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC4 | X | X |  | 132kV | ULK |  | Spare - Slot 2J/ Binary Input CC4 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC5 | X | X | X | 132kV | ULK | Control System Non Urgent | Plant Status Indications DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind5.stVal[ST] |  | 1085 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC6 | X | X | X | 132kV | ULK | Control System Non Urgent | CB Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind6.stVal[ST] |  | 1086 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC7 | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection & First Intertrip IED Defective | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind7.stVal[ST] |  | 1087 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC8 | X | X | X | 132kV | ULK | Control System Non Urgent | First Main Protection & First Intertrip DC Supply MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind8.stVal[ST] |  | 1088 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC9 | X | X | X | 132kV | ULK | Control System Non Urgent | First Main Protection GPS DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind9.stVal[ST] |  | 1089 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC10 | X | X | X | 132kV | ULK | Trip Relays Operated | First Main Protection Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind10.stVal[ST] |  | 1090 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC11 | X | X | X | 132kV | ULK | Trip Relays Operated | First Intertrip Receive Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind11.stVal[ST] |  | 1091 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC12 | X | X | X | 132kV | ULK | Conns Protection Urgent | Conns Fault Detection IED Defective | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind12.stVal[ST] |  | 1092 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC13 | X | X | X | 132kV | ULK | Control System Non Urgent | Conns Fault Detection DC Supply MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind13.stVal[ST] |  | 1093 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC14 | X | X | X | 132kV | ULK | Trip Relays Operated | Conns Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind14.stVal[ST] |  | 1094 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC15 | X | X | X | 132kV | ULK | Trip Relays Operated | LOM Trip Relay Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind15.stVal[ST] |  | 1095 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | Feeder Alarm | Slot 2J/ Binary Input CC16 | X | X | X | 132kV | ULK | Control System Non Urgent | First Main Protection GPS Fail | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind16.stVal[ST] |  | 1096 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot F / Binary Input CC9 | X | X | X | 132kV | ULK | Control System Non Urgent | 105 CB Selector Switch On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind9.stVal[ST] |  | 1008 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot F / Binary Input CC10 | X | X |  | 132kV | ULK |  | Spare - Slot F / Binary Input CC10 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind10.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot F / Binary Input CC14 | X | X |  | 132kV | ULK |  | 105 Manual Synch Selected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot F / Binary Input CC15 | X | X |  | 132kV | ULK |  | 105 Manual Override Close Selected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot F / Binary Input CC16 | X | X |  | 132kV | ULK |  | 105 Sync Close Contact Faulty | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO1.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO1/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot G / Binary Input CC1 | X | X |  | 132kV | ULK |  | 105 TRR Scheme Initiated | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot G / Binary Input CC2 | X | X |  | 132kV | ULK |  | 105 Trip Relay Reset Push Button Initiated | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind2.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot G / Binary Input CC3 | X | X |  | 132kV | ULK |  | Spare - Slot G / Binary Input CC3 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO2.Ind3.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO2/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot J / Binary Input CC17 | X | X |  | 132kV | ULK |  | Spare - Slot J/ Binary Input CC17 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind17.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind17/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | DAR In | X | X | X | 132kV | ULK | Indication | 105 DAR In | REM_CEL_OUT_IN | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind11.stVal[ST] |  | 1068 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | DAR Out | X | X | X | 132kV | ULK | Indication | 105 DAR Out | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind10.stVal[ST] |  | 1069 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Sync In Progress | X | X |  | 132kV | ULK |  | 105 Sync In Progress | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind32.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind32/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Sync Inhibit Active | X | X | X | 132kV | ULK | Control System Non Urgent | 105 Sync Inhibit Active | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind31.stVal[ST] |  | 1115 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind31/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | System Split Detected | X | X | X | 132kV | ULK | System Split | 105 System Split Detected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind34.stVal[ST] |  | 1116 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind34/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | Check Sync Out | X | X | X | 132kV | ULK | Check Sync Out | 105 Check Sync Out | REM_CEL_OUT_IN | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind1.stVal[ST] |  | 1117 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | Check Sync In | X | X | X | 132kV | ULK | Check Sync In | 105 Check Sync In | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind2.stVal[ST] |  | 1118 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | System Sync Out | X | X | X | 132kV | ULK | System Sync Out | 105 System Sync Out | REM_CEL_OUT_IN | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind3.stVal[ST] |  | 1119 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | System Sync In | X | X | X | 132kV | ULK | System Sync In | 105 System Sync In | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind4.stVal[ST] |  | 1120 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | System Sync IN - Awaiting Control | X | X |  | 132kV | ULK |  | 105 System Sync IN - Awaiting Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind30.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind30/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | System Sync IN - Awaiting Sync | X | X |  | 132kV | ULK |  | 105 System Sync IN - Awaiting Sync | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind33.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind33/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | System Sync Failed | X | X | X | 132kV | ULK | Control System Non Urgent | 105 Remote System Sync Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind41.stVal[ST] |  | 1121 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind41/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Check Sync Failed | X | X | X | 132kV | ULK | Control System Non Urgent | 105 Remote Check Sync Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind40.stVal[ST] |  | 1122 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind40/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Override Close Failed | X | X |  | 132kV | ULK |  | 105 Remote Override Close Failed | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind42.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind42/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Local Check Sync Failed | X | X |  | 132kV | ULK |  | 105 Local Check Sync Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Local Check Sync Active | X | X |  | 132kV | ULK |  | 105 Local Check Sync Active | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Local LBDL Synch Detected | X | X |  | 132kV | ULK |  | 105 Local LBDL Synch Detected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind24.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind24/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Local DBDL Synch Detected | X | X |  | 132kV | ULK |  | 105 Local DBDL Synch Detected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind25.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind25/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Local DBLL Synch Detected | X | X |  | 132kV | ULK |  | 105 Local DBLL Synch Detected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind26.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind26/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Local Close OK Signal | X | X |  | 132kV | ULK |  | 105 Local Close OK Signal | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | CB Failed To Close | X | X |  | 132kV | ULK |  | 105 CB Failed To Close | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind45.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind45/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | TRR Scheme Enabled | X | X |  | 132kV | ULK |  | 105 TRR Scheme Enabled | REM_ALM_OUT_IN | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind46.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind46/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | BCU Trip Relay Reset (TD10) | X | X | X | 132kV | ULK | Trip Relays Reset | 105 Trip Relay Reset (TD10) | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind12.stVal[ST] |  | 1123 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | BCU Trip Relay Reset (TD120) | X | X | X | 132kV | ULK | Trip Relays Reset | 105 Trip Relay Reset (TD120) | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind13.stVal[ST] |  | 1124 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR In Progress | X | X | X | 132kV | ULK | Circuit Breaker Urgent | DAR In Progress | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind35.stVal[ST] |  | 1125 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind35/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR DeadTime Enabled | X | X |  | 132kV | ULK |  | DAR DeadTime Enabled | REM_ALM_DIS_ENA | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR DeadTime Running | X | X |  | 132kV | ULK |  | DAR DeadTime Running | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR DeadTime Complete | X | X |  | 132kV | ULK |  | DAR DeadTime Complete | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | CB Close Command (DAR Close) | X | X |  | 132kV | ULK |  | CB Close Command (DAR Close) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind47.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind47/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR Reclaim Time Running | X | X |  | 132kV | ULK |  | DAR Reclaim Time Running | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Reclaim Timer Complete (DAR complete) | X | X |  | 132kV | ULK |  | Reclaim Timer Complete (DAR complete) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind43.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind43/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR CB Failed To Close | X | X | X | 132kV | ULK | Circuit Breaker Urgent | DAR CB Failed To Close | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind37.stVal[ST] |  | 1126 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind37/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | (DAR) 2nd Fault Detected | X | X | X | 132kV | ULK | DAR Lockout | (DAR) 2nd Fault Detected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind38.stVal[ST] |  | 1127 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind38/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | DAR Start | X | X |  | 132kV | ULK |  | DAR Start | REM_ALM_RST_START | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | CBR/CBR1 | Circuit Breaker Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 105 Circuit Breaker Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI1.Pos.stVal[ST] |  | 1000 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI1/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | CBR/CBR1 | Circuit Breaker Open/Close Contol | X | X | X | 132kV | ULK | Open/Close Control | 105 Circuit Breaker Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI1.Pos.Oper.ctlVal[CO] |  | 1000 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI1/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | CBR/CBR1 | Circuit Breaker Selected | X | X |  | 132kV | ULK |  | 105 Circuit Breaker Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI1.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI1/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2H/ Binary Input CC29 | X | X | X | 132kV | ULK | Circuit Breaker Urgent | 105 Trip Circuit Defective | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind29.stVal[ST] |  | 1077 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind29/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2H/ Binary Input CC30 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC30 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind30.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind30/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2H/ Binary Input CC31 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC31 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind31.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind31/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2H/ Binary Input CC32 | X | X |  | 132kV | ULK |  | Spare - Slot 2H/ Binary Input CC32 | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/GGIO5.Ind32.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO5/Ind32/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2J/ Binary Input CC1 | X | X | X | 132kV | ULK | Control System Non Urgent | 105 CB Trip & Close Circuit 1 DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind1.stVal[ST] |  | 1081 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2J/ Binary Input CC2 | X | X | X | 132kV | ULK | Control System Non Urgent | 105 CB Trip Circuit 2 DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind2.stVal[ST] |  | 1082 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | CBR/CBR1 | Slot 2J/ Binary Input CC3 | X | X | X | 132kV | ULK | Circuit Breaker Non Urgent | 105 Trip Relay Reset DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO6.Ind3.stVal[ST] |  | 1083 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO6/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | CBR/CBR1 | Reset Trip Relay | X | X | X | 132kV | ULK | Trip Relays Reset | 105 Reset Trip Relay | REM_CMD_RESET | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO38.Oper.ctlVal[CO] |  | 1008 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO38/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | CBR/CBR1 | Reset DAR Lockout | X | X | X | 132kV | ULK | Control | 105 Reset DAR Lockout | REM_CMD_RESET | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO39.Oper.ctlVal[CO] |  | 1009 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO39/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | CBR/CBR1 | Sync Cancel | X | X | X | 132kV | ULK | Control | 105 Sync Cancel | REM_CMD_CANCEL | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO35.Oper.ctlVal[CO] |  | 1014 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO35/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | CBR/CBR1 | Check Sync Out Control | X | X | X | 132kV | ULK | Control | 105 Check Sync Out | REM_CMD_IN_OUT | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO33.Oper.ctlVal[CO] |  | 1015 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO33/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | CBR/CBR1 | System Sync In Control | X | X | X | 132kV | ULK | Control | 105 System Sync In | REM_CMD_OUT_IN | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO34.Oper.ctlVal[CO] |  | 1016 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO34/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control - Out | CBR/CBR1 | DAR Out Control | X | X | X | 132kV | ULK | Control | 105 DAR Out | REM_CMD_OUT | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO36.Oper.ctlVal[CO] |  | 1017 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO36/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control - In | CBR/CBR1 | DAR In Control | X | X | X | 132kV | ULK | Control | 105 DAR In | REM_CMD_IN | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO37.Oper.ctlVal[CO] |  | 1018 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO37/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/ES3 | Slot H / Binary Input CC14 | X | X |  | 132kV | ULK | Control System Non Urgent | 101C On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/ES3 | Slot J / Binary Input CC25 | X | X | X | 132kV | ULK | Control System Non Urgent | 101C Motor DC MCB Trip/Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind25.stVal[ST] |  | 1036 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind25/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/ES3 | Earth Switch 3 Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 101C Earth Switch 3 Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI6.Pos.stVal[ST] |  | 1005 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI6/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | DIS/ES3 | Earth Switch 3 Open/Close Contol | X | X |  | 132kV | ULK | Open/Close Control | 101C Earth Switch 3 Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI6.Pos.Oper.ctlVal[CO] |  |  | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI6/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | DIS/ES3 | Earth Switch 3 Selected | X | X |  | 132kV | ULK |  | 101C Earth Switch 3 Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI6.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI6/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/ES4 | Slot H / Binary Input CC15 | X | X |  | 132kV | ULK | Control System Non Urgent | 101D On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/ES4 | Slot J / Binary Input CC24 | X | X | X | 132kV | ULK | Control System Non Urgent | 101D Motor DC MCB Trip/Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind24.stVal[ST] |  | 1035 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind24/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/ES4 | Earth Switch 4 Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 101D Earth Switch 4 Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI7.Pos.stVal[ST] |  | 1006 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI7/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | DIS/ES4 | Earth Switch 4 Open/Close Contol | X | X |  | 132kV | ULK | Open/Close Control | 101D Earth Switch 4 Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI7.Pos.Oper.ctlVal[CO] |  |  | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI7/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | DIS/ES4 | Earth Switch 4 Selected | X | X |  | 132kV | ULK |  | 101D Earth Switch 4 Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI7.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI7/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/DIS2 | Slot J / Binary Input CC22 | X | X | X | 132kV | ULK | Control System Non Urgent | 107 Motor DC MCB Trip/Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind22.stVal[ST] |  | 1033 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind22/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/DIS2 | Disconnector 2 Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 107 Disconnector 2 Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI3.Pos.stVal[ST] |  | 1002 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI3/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | DIS/DIS2 | Disconnector 2 Open/Close Contol | X | X | X | 132kV | ULK | Open/Close Control | 107 Disconnector 2 Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI3.Pos.Oper.ctlVal[CO] |  | 1002 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI3/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | DIS/DIS2 | Disconnector 2 Selected | X | X |  | 132kV | ULK |  | 107 Disconnector 2 Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI3.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI3/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/DIS2 | Slot H / Binary Input CC10 | X | X |  | 132kV | ULK | Control System Non Urgent | 107 On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind10.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/DIS1 | Slot J / Binary Input CC23 | X | X | X | 132kV | ULK | Control System Non Urgent | 103 Motor DC MCB Trip/Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind23.stVal[ST] |  | 1034 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind23/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/DIS1 | Disconnector 1 Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 103 Disconnector 1 Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI2.Pos.stVal[ST] |  | 1001 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI2/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | DIS/DIS1 | Disconnector 1 Open/Close Contol | X | X | X | 132kV | ULK | Open/Close Control | 103 Disconnector 1 Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI2.Pos.Oper.ctlVal[CO] |  | 1001 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI2/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | DIS/DIS1 | Disconnector 1 Selected | X | X |  | 132kV | ULK |  | 103 Disconnector 1 Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI2.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI2/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/DIS1 | Slot H / Binary Input CC9 | X | X |  | 132kV | ULK | Control System Non Urgent | 103 On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/ES2 | Slot J / Binary Input CC26 | X | X | X | 132kV | ULK | Control System Non Urgent | 101B Motor DC MCB Trip/Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind26.stVal[ST] |  | 1037 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind26/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/ES2 | Earth Switch 2 Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 101B Earth Switch 2 Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI5.Pos.stVal[ST] |  | 1004 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI5/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | DIS/ES2 | Earth Switch 2 Open/Close Contol | X | X |  | 132kV | ULK | Open/Close Control | 101B Earth Switch 2 Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI5.Pos.Oper.ctlVal[CO] |  |  | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI5/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | DIS/ES2 | Earth Switch 2 Selected | X | X |  | 132kV | ULK |  | 101B Earth Switch 2 Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI5.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI5/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/ES2 | Slot H / Binary Input CC12 | X | X |  | 132kV | ULK | Control System Non Urgent | 101B On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind12.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | DIS/ES1 | Slot J / Binary Input CC27 | X | X | X | 132kV | ULK | Control System Non Urgent | 101A Motor DC MCB Trip/Control DC MCB Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO4.Ind27.stVal[ST] |  | 1038 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO4/Ind27/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/ES1 | Earth Switch 1 Open/Closed | X | X | X | 132kV | ULK | Open/Close Indication | 101A Earth Switch 1 Open/Closed | REM_POS_SWG | ULK |  | CODED enum |  | USINT | CON/CSWI4.Pos.stVal[ST] |  | 1003 | 3 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI4/Pos/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | DIS/ES1 | Earth Switch 1 Open/Close Contol | X | X |  | 132kV | ULK | Open/Close Control | 101A Earth Switch 1 Open/Close Contol | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/CSWI4.Pos.Oper.ctlVal[CO] |  |  | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI4/Pos/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Select Control | DIS/ES1 | Earth Switch 1 Selected | X | X |  | 132kV | ULK |  | 101A Earth Switch 1 Selected | REM_SCT | ULK |  | BOOL |  | BOOL | CON/CSWI4.Pos.stSeld[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/CSWI4/Pos/stSeld[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | DIS/ES1 | Slot H / Binary Input CC11 | X | X |  | 132kV | ULK | Control System Non Urgent | 101A On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/GGIO3.Ind11.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/GGIO3/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | BCU Alarm | BCU Dummy Open | X | X | X | 132kV | ULK | Indication | Dummy CB Open | REM_POS_SWG | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind22.stVal[ST] |  | 1113 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind22/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Indication | BCU Alarm | BCU Dummy Closed | X | X | X | 132kV | ULK | Indication | Dummy CB Closed | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind23.stVal[ST] |  | 1114 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind23/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | BCU Health Status Failed | X | X | X | 132kV | ULK | Control System Urgent | BCU Fail | REM_ALM_ON_OFF | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind29.stVal[ST] |  | 1128 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind29/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | BCU Health Status Not Normal | X | X | X | 132kV | ULK | Control System Urgent | BCU Health Status Not Normal | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind28.stVal[ST] |  | 1129 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind28/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | BCU Restarted | X | X |  | 132kV | ULK |  | BCU Restarted | REM_NOT_REQUIRED | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind27.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind27/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | BCU On Local | X | X | X | 132kV | ULK | Control System Urgent | BCU On Local | REM_ALM_REM_LOC | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind49.stVal[ST] |  | 1130 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind49/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | BCU Controls Disabled | X | X | X | 132kV | ULK | Control System Urgent | BCU Controls Disabled | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind48.stVal[ST] |  | 1131 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind48/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | Red LAN Alarm | X | X | X | 132kV | ULK | Control System Urgent | BCU Red LAN Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind19.stVal[ST] |  | 1132 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | Black LAN Alarm | X | X | X | 132kV | ULK | Control System Urgent | BCU Black LAN Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind20.stVal[ST] |  | 1133 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind20/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Alarm | BCU Alarm | Internal Clock Faulty | X | X | X | 132kV | ULK | Control System Urgent | Clock Synchronisation Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CON/eveGGIO1.Ind21.stVal[ST] |  | 1134 | 1 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/eveGGIO1/Ind21/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | BCU Control | BCU Dummy Open | X | X | X | 132kV | ULK | Control | Dummy CB Open | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO42.Oper.ctlVal[CO] |  | 1012 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO42/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Control | BCU Control | BCU Dummy Close | X | X | X | 132kV | ULK | Control | Dummy CB Close | REM_CMD_SWG | ULK |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO43.Oper.ctlVal[CO] |  | 1013 | 12 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/vinGGIO1/SPCSO43/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Running Voltage | X | X | X | 132kV | ULK |  | 105 Running Voltage | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.AuxV.cVal.mag.f[MX] |  | 1003 | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/AuxV/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Incoming R-N | X | X |  | 132kV | ULK |  | 105 Incoming Voltage R-N | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.PhV.phsA.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/PhV.phsA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Incoming Y-N | X | X |  | 132kV | ULK |  | 105 Incoming Voltage Y-N | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.PhV.phsB.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/PhV.phsB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Incoming B-N | X | X |  | 132kV | ULK |  | 105 Incoming Voltage B-N | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.PhV.phsC.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/PhV.phsC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Phase R-Y Voltage | X | X |  | 132kV | ULK |  | 105 Ph-Ph Voltage R-Y | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.PPV.phsAB.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/PPV.phsAB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Phase Y-B Voltage | X | X | X | 132kV | ULK |  | 105 Ph-Ph Voltage Y-B | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.PPV.phsBC.cVal.mag.f[MX] |  | 1008 | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/PPV.phsBC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Phase B-R Voltage | X | X |  | 132kV | ULK |  | 105 Ph-Ph Voltage B-R | REM_NOT_REQUIRED | ULK |  | VECTOR |  | REAL | CON/MMXU1.PPV.phsCA.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/PPV.phsCA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Current Red | X | X |  | 132kV | ULK |  | 105 Current Red | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | CON/MMXU1.A.phsA.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/A.phsA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Current Yellow | X | X | X | 132kV | ULK |  | 105 Current Yellow | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | CON/MMXU1.A.phsB.cVal.mag.f[MX] |  | 1010 | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/A.phsB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Current Blue | X | X |  | 132kV | ULK |  | 105 Current Blue | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | CON/MMXU1.A.phsC.cVal.mag.f[MX] |  |  | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/A.phsC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Watts | X | X | X | 132kV | ULK |  | 105 MW | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | CON/MMXU1.TotW.mag.f[MX] |  | 1013 | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/TotW/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | VAr | X | X | X | 132kV | ULK |  | 105 Mvar | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | CON/MMXU1.TotVAr.mag.f[MX] |  | 1014 | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/TotVAr/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | C650 | 192.168.248.15 /23 | BCU01 | LIMKE01BCU01 | Analog | Analogue | Frequency | X | X | X | 132kV | ULK |  | 105 Hz | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | CON/MMXU1.Hz.mag.f[MX] |  | 1015 | 30 | [5 empty] | LIMKE01BCU01!LIMKE01BCU01CON/MMXU1/Hz/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection On Local Control | X | X | X | 132kV | ULK | First Main Protection Non Urgent | First Main Protection On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/LedGGIO1.Ind9.stVal[ST] |  | 300 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/LedGGIO1/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Any Phase) Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Trip (Any Phase) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | System/LedGGIO1.Ind2.stVal[ST] |  | 301 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/LedGGIO1/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Indication | First Main Protection Alarms | First Main Protection Out of Service | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Out of Service | REM_ALM_IN_OUT | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind9.stVal[ST] |  | 302 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection GPS Sync Failed | X | X | X | 132kV | ULK | First Main Protection Non Urgent | First Main Protection GPS Sync Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind5.stVal[ST] |  | 303 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection (Route A) Comms Failed | X | X | X | 132kV | ULK | First Main Protection Comms Non Urgent | First Main Protection (Route A) Comms Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind6.stVal[ST] |  | 304 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection (Route B) Comms Failed | X | X | X | 132kV | ULK | First Main Protection Comms Non Urgent | First Main Protection (Route B) Comms Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind7.stVal[ST] |  | 305 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Indication | First Main Protection Alarms | First Intertrip Out of Service | X | X | X | 132kV | ULK | First Intertrip Urgent | First Intertrip Out of Service | REM_ALM_IN_OUT | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind2.stVal[ST] |  | 306 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Intertrip on Test | X | X | X | 132kV | ULK | First Intertrip Urgent | First Intertrip on Test | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind3.stVal[ST] |  | 307 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Indication | First Main Protection Alarms | First Main Protection Loss of Mains Intertrip Out of Service | X | X | X | 132kV | ULK | First Intertrip Urgent | First Main Protection Loss of Mains Intertrip Out of Service | REM_CEL_IN_OUT | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind16.stVal[ST] |  | 308 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection DAR Lockout | X | X | X | 132kV | ULK | DAR Lockout | First Main Protection DAR Lockout | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind8.stVal[ST] |  | 309 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Broken Conductor Alarm | X | X | X | 132kV | ULK | Broken Conductor | First Main Protection Broken Conductor Alarm | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/RlyGGIO1.Ind13.stVal[ST] |  | 310 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/RlyGGIO1/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/LLN0.Beh.stVal[ST] |  | 300 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/LLN0/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Differential Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DifPDIF1.Beh.stVal[ST] |  | 301 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Differential Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Op.general[ST] |  | 311 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential (R Phase) Protection Operated | X | X |  | 132kV | ULK |  | First Main Protection Differential (R Phase) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Op.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Op/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential (Y Phase) Protection Operated | X | X |  | 132kV | ULK |  | First Main Protection Differential (Y Phase) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Op.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Op/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential (B Phase) Protection Operated | X | X |  | 132kV | ULK |  | First Main Protection Differential (B Phase) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Op.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Op/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Differential Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential (R Phase) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Differential (R Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Str.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Str/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential (Y Phase) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Differential (Y Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Str.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Str/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential (B Phase) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Differential (B Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DifPDIF1.Str.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DifPDIF1/Str/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Differential Protection Out of Service | X | X | X | 132kV | ULK | First Main Protection Non Urgent | First Main Protection Differential Protection Out of Service | REM_ALM_IN_OUT_OOS | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind10.stVal[ST] |  | 312 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Aided Distance Protection Out of Service | X | X | X | 132kV | ULK | First Main Protection Non Urgent | First Main Protection Aided Distance Protection Out of Service | REM_ALM_IN_OUT_OOS | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind11.stVal[ST] |  | 313 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Plain Distance Protection Out of Service | X | X | X | 132kV | ULK | First Main Protection Non Urgent | First Main Protection Plain Distance Protection Out of Service | REM_ALM_IN_OUT_OOS | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind12.stVal[ST] |  | 314 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (R Phase) | X | X |  | 132kV | ULK |  | First Main Protection Distance Trip (R Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Y Phase) | X | X |  | 132kV | ULK |  | First Main Protection Distance Trip (Y Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (B Phase) | X | X |  | 132kV | ULK |  | First Main Protection Distance Trip (B Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Neutral) | X | X |  | 132kV | ULK |  | First Main Protection Distance Trip (Neutral) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Neutral) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Neutral) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (R Phase) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (R Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Y Phase) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Y Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind2.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (B Phase) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (B Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind3.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Feeder End Protection Active | X | X |  | 132kV | ULK |  | First Main Protection Feeder End Protection Active | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Intertrip Operated | X | X | X | 132kV | ULK | First Intertrip Operated | First Intertrip Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind15.stVal[ST] |  | 315 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Loss of Mains Intertrip Receive | X | X | X | 132kV | ULK | First Intertrip Operated | First Main Protection Loss of Mains Intertrip Receive | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind14.stVal[ST] |  | 316 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | 3 to 2 Ended Reconfiguration (Local) | X | X |  | 132kV | ULK |  | 3 to 2 Ended Reconfiguration (Local) | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | System/GosGGIO2.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/GosGGIO2/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Aided Distance Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Aided Distance Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DisPSCH1.Beh.stVal[ST] |  | 302 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPSCH1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Aided Trip | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Aided Trip | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DisPSCH1.Op.general[ST] |  | 317 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPSCH1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Aided Signal Send | X | X |  | 132kV | ULK |  | First Main Protection Distance Aided Signal Send | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | Protection/DisPSCH1.ProTx.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPSCH1/ProTx/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Aided Signal Receive | X | X |  | 132kV | ULK |  | First Main Protection Distance Aided Signal Receive | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | Protection/DisPSCH1.ProRx.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPSCH1/ProRx/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Aided Channel Fail | X | X |  | 132kV | ULK |  | First Main Protection Distance Aided Channel Fail | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | Protection/DisPSCH1.LosOfGrd.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPSCH1/LosOfGrd/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance (Z1) Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Distance (Z1) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DisPDIS1.Beh.stVal[ST] |  | 303 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Z1) Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Trip (Z1) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DisPDIS1.Op.general[ST] |  | 318 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Z1) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Z1) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DisPDIS1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance (Z2) Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Distance (Z2) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DisPDIS2.Beh.stVal[ST] |  | 304 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS2/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Z2) Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Trip (Z2) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DisPDIS2.Op.general[ST] |  | 319 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Z2) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Z2) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DisPDIS2.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS2/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance (Z3) Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Distance (Z3) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DisPDIS3.Beh.stVal[ST] |  | 305 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS3/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Z3) Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Trip (Z3) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DisPDIS3.Op.general[ST] |  | 320 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS3/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Z3) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Z3) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DisPDIS3.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS3/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance (Z4) Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Distance (Z4) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DisPDIS4.Beh.stVal[ST] |  | 306 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS4/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Z4) Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Trip (Z4) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DisPDIS4.Op.general[ST] |  | 321 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS4/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Z4) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Z4) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DisPDIS4.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS4/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance (Z5) Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Distance (Z5) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/DisPDIS5.Beh.stVal[ST] |  | 307 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS5/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Distance Trip (Z5) Protection Operated | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Distance Trip (Z5) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/DisPDIS5.Op.general[ST] |  | 322 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS5/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Distance Start (Z5) Protection Start | X | X |  | 132kV | ULK |  | First Main Protection Distance Start (Z5) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/DisPDIS5.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/DisPDIS5/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Switch On To Fault Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Switch On To Fault Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/SofPSOF1.Beh.stVal[ST] |  | 308 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Switch On To Fault Active | X | X |  | 132kV | ULK | First Main Protection Operated | First Main Protection Switch On To Fault Active | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/SofPSOF1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Switch On To Fault Trip (Z1) | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Switch On To Fault Trip (Z1) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/SofPSOF1.Op1.general[ST] |  | 324 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Op1/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Switch On To Fault Trip (Z2) | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Switch On To Fault Trip (Z2) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/SofPSOF1.Op2.general[ST] |  | 325 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Op2/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Switch On To Fault Trip (Z3) | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Switch On To Fault Trip (Z3) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/SofPSOF1.Op3.general[ST] |  | 326 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Op3/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Switch On To Fault Trip (Z4) | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Switch On To Fault Trip (Z4) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/SofPSOF1.Op4.general[ST] |  | 327 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Op4/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Switch On To Fault Trip (Z5) | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Switch On To Fault Trip (Z5) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/SofPSOF1.Op5.general[ST] |  | 328 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/SofPSOF1/Op5/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Feeder End Protection Start (Any Phase) | X | X |  | 132kV | ULK |  | First Main Protection Feeder End Protection Start (Any Phase) | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | Protection/OcpPTOC1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/OcpPTOC1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Feeder End Protection Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Feeder End Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/OcpPTOC1.Beh.stVal[ST] |  | 309 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/OcpPTOC1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Feeder End Protection Trip (Any Phase) | X | X | X | 132kV | ULK | First Main Protection Operated | First Main Protection Feeder End Protection Trip (Any Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/OcpPTOC1.Op.general[ST] |  | 329 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/OcpPTOC1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Overvoltage Stage 1 Operated | X | X | X | 132kV | ULK | First Main Protection Overvoltage Stage 1 | First Main Protection Overvoltage Stage 1 Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/VtpPhsPTOV1.Op.general[ST] |  | 330 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTOV1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Overvoltage Stage 1 Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Overvoltage Stage 1 Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/VtpPhsPTOV1.Beh.stVal[ST] |  | 310 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTOV1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Overvoltage Stage 2 Operated | X | X | X | 132kV | ULK | First Main Protection Overvoltage Stage 2 | First Main Protection Overvoltage Stage 2 Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/VtpPhsPTOV2.Op.general[ST] |  | 331 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTOV2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Overvoltage Stage 2 Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Overvoltage Stage 2 Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/VtpPhsPTOV2.Beh.stVal[ST] |  | 311 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTOV2/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Undervoltage Stage 1 Operated | X | X | X | 132kV | ULK | First Main Protection Undervoltage Stage 1 | First Main Protection Undervoltage Stage 1 Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/VtpPhsPTUV1.Op.general[ST] |  | 332 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTUV1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Undervoltage Stage 1 Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Undervoltage Stage 1 Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/VtpPhsPTUV1.Beh.stVal[ST] |  | 312 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTUV1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Undervoltage Stage 2 Operated | X | X | X | 132kV | ULK | First Main Protection Undervoltage Stage 2 | First Main Protection Undervoltage Stage 2 Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | Protection/VtpPhsPTUV2.Op.general[ST] |  | 333 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTUV2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Undervoltage Stage 2 Disabled | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Undervoltage Stage 2 Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Protection/VtpPhsPTUV2.Beh.stVal[ST] |  | 313 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPProtection/VtpPhsPTUV2/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Intertrip Send (Route A) | X | X |  | 132kV | ULK |  | First Intertrip Send (Route A) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/ImfOutGGIO1.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/ImfOutGGIO1/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Intertrip Send (Route B) | X | X |  | 132kV | ULK |  | First Intertrip Send (Route B) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/ImfOutGGIO2.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/ImfOutGGIO2/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Intertrip Receive (Route A) | X | X |  | 132kV | ULK |  | First Intertrip Receive (Route A) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/ImfInpGGIO1.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/ImfInpGGIO1/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | 3 to 2 Ended Reconfiguration (Remote 1) | X | X |  | 132kV | ULK |  | 3 to 2 Ended Reconfiguration (Remote 1) | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | System/ImfInpGGIO1.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/ImfInpGGIO1/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Intertrip Receive (Route B) | X | X |  | 132kV | ULK |  | First Intertrip Receive (Route B) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/ImfInpGGIO2.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/ImfInpGGIO2/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | 3 to 2 Ended Reconfiguration (Remote 2) | X | X |  | 132kV | ULK |  | 3 to 2 Ended Reconfiguration (Remote 2) | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | System/ImfInpGGIO2.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/ImfInpGGIO2/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Loss of Mains Intertrip Send | X | X | X | 132kV | ULK | First Intertrip Operated | First Main Protection Loss of Mains Intertrip Send | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/OptGGIO1.Ind24.stVal[ST] |  | 334 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/OptGGIO1/Ind24/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection & First Intertrip IED Clock Synchronisation Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | First Main Protection & First Intertrip IED Clock Synchronisation Alarm | REM_ALM_ON_OFF | ULK |  | BOOL |  | BOOL | System/LLN0.SyncSt.stVal[ST] |  | 335 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/LLN0/SyncSt/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Event | First Main Protection Alarms | First Main Protection Disturbance Record Available | X | X |  | 132kV | ULK |  | First Main Protection Disturbance Record Available | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | Records/RDRE1.RcdMade.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPRecords/RDRE1/RcdMade/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection VT Failed | X | X | X | 132kV | ULK | First Main Protection Non Urgent | First Main Protection VT Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | System/AlmGGIO1.Alm6.stVal[ST] |  | 336 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/AlmGGIO1/Alm6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Power Swing Detection Disabled | X | X | X | 132kV | ULK | Power Swing Blocking Detected | First Main Protection Power Swing Detection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | Control/PsbRPSB1.Beh.stVal[ST] |  | 314 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPControl/PsbRPSB1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Alarm | First Main Protection Alarms | First Main Protection Power Swing Detected | X | X | X | 132kV | ULK | First Main Protection Urgent | First Main Protection Power Swing Detected | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | Control/PsbRPSB1.Str1.general[ST] |  | 337 | 1 | [5 empty] | LIMKE01FMP!LIMKE01FMPControl/PsbRPSB1/Str1/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Control - Out | First Main Protection Controls | First Main Protection Out Control | X | X | X | 132kV | ULK |  | First Main Protection Out Control | REM_CMD_OUT | ULK |  | BOOL |  | BOOL | System/PloGGIO1.SPCSO28.Oper.ctlVal[CO] |  | 300 | 12 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/PloGGIO1/SPCSO28/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Control - In | First Main Protection Controls | First Main Protection In Control | X | X | X | 132kV | ULK |  | First Main Protection In Control | REM_CMD_IN | ULK |  | BOOL |  | BOOL | System/PloGGIO1.SPCSO29.Oper.ctlVal[CO] |  | 301 | 12 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/PloGGIO1/SPCSO29/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Control - Out | First Main Protection Controls | First Intertrip Out Control | X | X | X | 132kV | ULK |  | First Intertrip Out Control | REM_CMD_OUT | ULK |  | BOOL |  | BOOL | System/PloGGIO1.SPCSO31.Oper.ctlVal[CO] |  | 302 | 12 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/PloGGIO1/SPCSO31/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Control - In | First Main Protection Controls | First Intertrip In Control | X | X | X | 132kV | ULK |  | First Intertrip In Control | REM_CMD_IN | ULK |  | BOOL |  | BOOL | System/PloGGIO1.SPCSO30.Oper.ctlVal[CO] |  | 303 | 12 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/PloGGIO1/SPCSO30/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Control - Out | First Main Protection Controls | First Main Protection Loss of Mains Intertrip Out Control | X | X | X | 132kV | ULK |  | First Main Protection Loss of Mains Intertrip Out Control | REM_CMD_OUT | ULK |  | BOOL |  | BOOL | System/PloGGIO1.SPCSO27.Oper.ctlVal[CO] |  | 304 | 12 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/PloGGIO1/SPCSO27/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Control - In | First Main Protection Controls | First Main Protection Loss of Mains Intertrip In Control | X | X | X | 132kV | ULK |  | First Main Protection Loss of Mains Intertrip In Control | REM_CMD_IN | ULK |  | BOOL |  | BOOL | System/PloGGIO1.SPCSO26.Oper.ctlVal[CO] |  | 305 | 12 | [5 empty] | LIMKE01FMP!LIMKE01FMPSystem/PloGGIO1/SPCSO26/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | P545 | 192.168.248.16 /23 | P545_REV9_FMP | LIMKE01FMP | Analog | First Main Protection Measurements | First Main Protection Fault Location | X | X | X | 132kV | ULK |  | First Main Protection Fault Location | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | Records/RFLO1.FltDiskm.mag.f[MX] |  | 315 | 30 | [5 empty] | LIMKE01FMP!LIMKE01FMPRecords/RFLO1/FltDiskm/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Operated | X | X | X | 132kV | ULK | Protection Operated | HV Connections 1 Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/A8750PDIF1.Op.general[ST] |  | 640 | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/A8750PDIF1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Operated (R Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 Protection Operated (R Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/A8750PDIF1.Op.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/A8750PDIF1/Op/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Operated (Y Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 Protection Operated (Y Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/A8750PDIF1.Op.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/A8750PDIF1/Op/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Operated (B Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 Protection Operated (B Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/A8750PDIF1.Op.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/A8750PDIF1/Op/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Differential Protection Disabled | X | X | X | 132kV | ULK | Protection Urgent | HV Connections 1 Differential Protection Disabled | REM_ALM_IN_OUT_15 | ULK |  | ENUM |  | USINT | PROT/A8750PDIF1.Beh.stVal[ST] |  | 640 | 30 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/A8750PDIF1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Operated | X | X | X | 132kV | ULK | CT Urgent | HV Connections 1 CT Supervision Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Op.general[ST] |  | 641 | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Operated (R Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Operated (R Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Op.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Op/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Operated (Y Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Operated (Y Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Op.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Op/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Operated (B Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Operated (B Phase) | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Op.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Op/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Start | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Start (R Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Start (R Phase) | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Str.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Str/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Start (Y Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Start (Y Phase) | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Str.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Str/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Start (B Phase) | X | X |  | 132kV | ULK |  | HV Connections 1 CT Supervision Start (B Phase) | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/CT50PTOC1.Str.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Str/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection CT Supervision Out of Service | X | X | X | 132kV | ULK | Protection Urgent | HV Connections 1 Protection CT Supervision Out of Service | REM_ALM_IN_OUT_15 | ULK |  | ENUM |  | USINT | PROT/CT50PTOC1.Beh.stVal[ST] |  | 641 | 30 | [5 empty] | LIMKE01CON!LIMKE01CONPROT/CT50PTOC1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection DAR Lockout | X | X | X | 132kV | ULK | DAR Lockout | HV Connections 1 DAR Lockout | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/Alm32GGIO1.Ind1.stVal[ST] |  | 642 | 1 | [5 empty] | LIMKE01CON!LIMKE01CONCTRL/Alm32GGIO1/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Event | CON Alarm | Connections Protection Disturbance Record Available | X | X |  | 132kV | ULK |  | HV Connections 1 Disturbance Record Available | REM_CEL_ON_OFF | ULK |  | BOOL |  | BOOL | DR/RDRE1.RcdMade.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01CON!LIMKE01CONDR/RDRE1/RcdMade/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Red LAN Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | HV Connections 1 Red LAN Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CTRL/V16GGIO1.Ind1.stVal[ST] |  | 643 | 1 | [5 empty] | LIMKE01CON!LIMKE01CONCTRL/V16GGIO1/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | 7SR230 | 192.168.248.17 /23 | 7SR2302_CON | LIMKE01CON | Alarm | CON Alarm | Connections Protection Black LAN Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | HV Connections 1 Black LAN Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | CTRL/V16GGIO1.Ind2.stVal[ST] |  | 644 | 1 | [5 empty] | LIMKE01CON!LIMKE01CONCTRL/V16GGIO1/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection On Local Control | X | X | X | 132kV | ULK | Second Main Protection Non Urgent | Second Main Protection On Local Control | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/PROTLGGIO1.SPCSO42.stVal[ST] |  | 360 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/PROTLGGIO1/SPCSO42/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Indication | Second Main Protection Alarms | Second Main Protection Out of Service | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Out of Service | REM_ALM_IN_OUT | ULK |  | BOOL |  | BOOL | CTRL/PRTOOSGGIO1.SPCSO44.stVal[ST] |  | 361 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/PRTOOSGGIO1/SPCSO44/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Differential Protection Out of Service | X | X | X | 132kV | ULK | Second Main Protection Non Urgent | Second Main Protection Differential Protection Out of Service | REM_ALM_IN_OUT_OOS | ULK |  | BOOL |  | BOOL | CTRL/DIFBLKGGIO2.SPCSO19.stVal[ST] |  | 362 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/DIFBLKGGIO2/SPCSO19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Differential Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Differential Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PTRC3.Op.general[ST] |  | 363 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC3/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Differential Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Differential Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC3.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC3/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Differential (R Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Differential (R Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC3.Str.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC3/Str/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Differential (Y Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Differential (Y Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC3.Str.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC3/Str/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Differential (B Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Differential (B Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC3.Str.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC3/Str/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection GPS Sync Failed | X | X | X | 132kV | ULK | Second Main Protection Non Urgent | Second Main Protection GPS Sync Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/GPSFLGGIO1.SPCSO1.stVal[ST] |  | 367 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/GPSFLGGIO1/SPCSO1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection (Route A) Comms Failed | X | X | X | 132kV | ULK | Second Main Protection Comms Non Urgent | Second Main Protection (Route A) Comms Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/RUTAFLGGIO1.SPCSO2.stVal[ST] |  | 368 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/RUTAFLGGIO1/SPCSO2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection (Route B) Comms Failed | X | X | X | 132kV | ULK | Second Main Protection Comms Non Urgent | Second Main Protection (Route B) Comms Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/RUTBFLGGIO1.SPCSO3.stVal[ST] |  | 369 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/RUTBFLGGIO1/SPCSO3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Plain Distance Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Non Urgent | Second Main Protection Plain Distance Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PTRC2.Mod.stVal[ST] |  | 361 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Mod/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Any Phase) Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Trip (Any Phase) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PTRC2.Op.general[ST] |  | 370 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Any Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Any Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC2.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Neutral) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Neutral) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC2.Str.neut[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Str/neut[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (R Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (R Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC2.Str.phsA[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Str/phsA[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Y Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Y Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC2.Str.phsB[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Str/phsB[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (B Phase) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (B Phase) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTRC2.Str.phsC[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTRC2/Str/phsC[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z1) Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Trip (Z1) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PDIS1.Op.general[ST] |  | 371 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z1) Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Distance Trip (Z1) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PDIS1.Beh.stVal[ST] |  | 362 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Z1) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Z1) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PDIS1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z2) Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Trip (Z2) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PDIS2.Op.general[ST] |  | 372 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS2/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z2) Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Distance Trip (Z2) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PDIS2.Beh.stVal[ST] |  | 363 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS2/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Z2) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Z2) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PDIS2.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS2/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z3) Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Trip (Z3) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PDIS3.Op.general[ST] |  | 373 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS3/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z3) Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Distance Trip (Z3) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PDIS3.Beh.stVal[ST] |  | 364 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS3/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Z3) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Z3) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PDIS3.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS3/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z4) Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Trip (Z4) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PDIS4.Op.general[ST] |  | 374 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS4/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z4) Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Distance Trip (Z4) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PDIS4.Beh.stVal[ST] |  | 365 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS4/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Z4) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Z4) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PDIS4.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS4/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z5) Protection Operated | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Trip (Z5) Protection Operated | REM_ALM_RST_OPTD | ULK |  | BOOL |  | BOOL | PROT/PDIS5.Op.general[ST] |  | 375 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS5/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Trip (Z5) Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Distance Trip (Z5) Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PDIS5.Beh.stVal[ST] |  | 366 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS5/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Start (Z5) Protection Start | X | X |  | 132kV | ULK |  | Second Main Protection Distance Start (Z5) Protection Start | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PDIS5.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PDIS5/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Aided Trip | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Distance Aided Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/AIDDIZGGIO1.SPCSO8.stVal[ST] |  | 376 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/AIDDIZGGIO1/SPCSO8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Aided Signal Send | X | X |  | 132kV | ULK |  | Second Main Protection Distance Aided Signal Send | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | PROT/PSCH1.ProTx.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PSCH1/ProTx/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Aided Signal Receive | X | X |  | 132kV | ULK |  | Second Main Protection Distance Aided Signal Receive | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | PROT/PSCH1.ProRx.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PSCH1/ProRx/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Aided Distance Protection Disabled | X | X | X | 132kV | ULK | Second Main Protection Non Urgent | Second Main Protection Aided Distance Protection Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PSCH1.Mod.stVal[ST] |  | 360 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PSCH1/Mod/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Distance Aided Channel Fail | X | X |  | 132kV | ULK |  | Second Main Protection Distance Aided Channel Fail | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/DICRFLGGIO1.SPCSO1.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/DICRFLGGIO1/SPCSO1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Event | Second Main Protection Alarms | Second Main Protection Feeder End Protection Active | X | X |  | 132kV | ULK |  | Second Main Protection Feeder End Protection Active | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | PROT/PTOC4.Mod.stVal[ST] |  |  | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTOC4/Mod/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Feeder End Protection Start (Any Phase) | X | X |  | 132kV | ULK |  | Second Main Protection Feeder End Protection Start (Any Phase) | REM_CEL_RST_START | ULK |  | BOOL |  | BOOL | PROT/PTOC4.Str.general[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/PTOC4/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Feeder End Protection Trip (Any Phase) | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Feeder End Protection Trip (Any Phase) | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/ENDFLTGGIO1.SPCSO4.stVal[ST] |  | 378 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ENDFLTGGIO1/SPCSO4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection DAR Lockout | X | X | X | 132kV | ULK | DAR Lockout | Second Main Protection DAR Lockout | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/DARLOGGIO1.SPCSO10.stVal[ST] |  | 379 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/DARLOGGIO1/SPCSO10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Event | Second Main Protection Alarms | Second Main Protection Disturbance Record Available | X | X |  | 132kV | ULK |  | Second Main Protection Disturbance Record Available | REM_CEL_OFF_ON | ULK |  | BOOL |  | BOOL | DR/RDRE1.RcdMade.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPDR/RDRE1/RcdMade/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection VT Failed | X | X | X | 132kV | ULK | Second Main Protection Non Urgent | Second Main Protection VT Failed | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/VTTRPGGIO1.SPCSO57.stVal[ST] |  | 380 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/VTTRPGGIO1/SPCSO57/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Broken Conductor Alarm | X | X | X | 132kV | ULK | Broken Conductor | Second Main Protection Broken Conductor Alarm | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/PHUNBGGIO1.SPCSO7.stVal[ST] |  | 381 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/PHUNBGGIO1/SPCSO7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Broken Conductor Alarm Disabled | X | X | X | 132kV | ULK | Second Main Protection Urgent | Second Main Protection Broken Conductor Alarm Disabled | REM_ALM_ENA_DIS_15 | ULK |  | ENUM |  | USINT | CTRL/PHUNBGGIO1.Beh.stVal[ST] |  | 368 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/PHUNBGGIO1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Indication | Second Main Protection Alarms | Second Intertrip Out of Service | X | X | X | 132kV | ULK | Second Intertrip Urgent | Second Intertrip Out of Service | REM_CEL_IN_OUT | ULK |  | BOOL |  | BOOL | CTRL/ITOOSGGIO1.SPCSO45.stVal[ST] |  | 382 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ITOOSGGIO1/SPCSO45/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Intertrip Send | X | X |  | 132kV | ULK |  | Second Intertrip Send | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/ITSNDGGIO2.SPCSO63.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ITSNDGGIO2/SPCSO63/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Intertrip Receive | X | X |  | 132kV | ULK |  | Second Intertrip Receive | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/ITRCVGGIO2.SPCSO64.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ITRCVGGIO2/SPCSO64/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Intertrip on Test | X | X | X | 132kV | ULK | Second Intertrip Urgent | Second Intertrip on Test | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | CTRL/ITTSTGGIO1.SPCSO63.stVal[ST] |  | 383 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ITTSTGGIO1/SPCSO63/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection & Second Intertrip IED Red LAN Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection & Second Intertrip IED Red LAN Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | EXT/pdGGIO32768.SPCSO2.stVal[ST] |  | 384 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPEXT/pdGGIO32768/SPCSO2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection & Second Intertrip IED Black LAN Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection & Second Intertrip IED Black LAN Alarm | REM_ALM_NOR_ALM | ULK |  | BOOL |  | BOOL | EXT/pdGGIO32768.SPCSO3.stVal[ST] |  | 385 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPEXT/pdGGIO32768/SPCSO3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection & Second Intertrip IED Clock Synchronisation Alarm | X | X | X | 132kV | ULK | Control System Non Urgent | Second Main Protection & Second Intertrip IED Clock Synchronisation Alarm | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | EXT/pdGGIO2.SPCSO4.stVal[ST] |  | 386 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPEXT/pdGGIO2/SPCSO4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Indication | Second Main Protection Alarms | Second Main Protection Switch On To Fault Active | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Switch On To Fault Active | REM_CEL_IN_OUT | ULK |  | ENUM |  | USINT | EXT/pdGGIO67.SPCSO49.stVal[ST] |  |  | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPEXT/pdGGIO67/SPCSO49/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Switch On To Fault Pickup | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Switch On To Fault Pickup | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | EXT/pdGGIO67.SPCSO57.stVal[ST] |  |  | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPEXT/pdGGIO67/SPCSO57/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Alarm | Second Main Protection Alarms | Second Main Protection Switch On To Fault Trip | X | X | X | 132kV | ULK | Second Main Protection Operated | Second Main Protection Switch On To Fault Trip | REM_ALM_OFF_ON | ULK |  | BOOL |  | BOOL | EXT/pdGGIO68.SPCSO5.stVal[ST] |  | 377 | 1 | [5 empty] | LIMKE01SMP!LIMKE01SMPEXT/pdGGIO68/SPCSO5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Control - Out | Second Main Protection Controls | Second Main Protection Out Control | X | X | X | 132kV | ULK |  | Second Main Protection Out Control | REM_CMD_OUT | ULK |  | BOOL |  | BOOL | CTRL/PRTOUTGAPC7.SPCSO.Oper.ctlVal[CO] |  | 360 | 12 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/PRTOUTGAPC7/SPCSO/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Control - In | Second Main Protection Controls | Second Main Protection In Control | X | X | X | 132kV | ULK |  | Second Main Protection In Control | REM_CMD_IN | ULK |  | BOOL |  | BOOL | CTRL/PRTINGAPC8.SPCSO.Oper.ctlVal[CO] |  | 361 | 12 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/PRTINGAPC8/SPCSO/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Control - In | Second Main Protection Controls | Second Intertrip In Control | X | X | X | 132kV | ULK |  | Second Intertrip In Control | REM_CMD_IN | ULK |  | BOOL |  | BOOL | CTRL/ITINGAPC9.SPCSO.Oper.ctlVal[CO] |  | 362 | 12 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ITINGAPC9/SPCSO/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Control - Out | Second Main Protection Controls | Second Intertrip Out Control | X | X | X | 132kV | ULK |  | Second Intertrip Out Control | REM_CMD_OUT | ULK |  | BOOL |  | BOOL | CTRL/ITOUTGAPC10.SPCSO.Oper.ctlVal[CO] |  | 363 | 12 | [5 empty] | LIMKE01SMP!LIMKE01SMPCTRL/ITOUTGAPC10/SPCSO/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Doureay | 01 | ULK |  | Siprotec-7SDx | 192.168.248.18 /23 | 7SD522_SMP | LIMKE01SMP | Analog | Second Main Protection Measurements | Second Main Protection Fault Location | X | X | X | 132kV | ULK |  | Second Main Protection Fault Location | REM_NOT_REQUIRED | ULK |  | FLOAT |  | REAL | PROT/RFLO1.FltDiskm.mag.f[MX] |  | 369 | 30 | [5 empty] | LIMKE01SMP!LIMKE01SMPPROT/RFLO1/FltDiskm/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC1 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC1 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC2 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC2 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind2.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC3 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC3 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind3.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC4 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC4 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC5 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC5 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC6 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC6 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC7 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC7 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC8 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC8 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC9 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC9 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC10 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC10 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind10.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC11 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC11 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind11.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC12 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC12 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind12.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC13 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC13 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC14 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC14 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC15 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC15 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot F / Binary Input CC16 | X | X |  | 132kV | COM |  | Spare - Slot F / Binary Input CC16 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO1.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO1/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC1 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC1 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC2 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC2 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind2.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC3 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC3 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind3.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC4 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC4 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC5 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC5 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC6 | X | X |  | 132kV | COM |  | BCU Control Switch Isolated | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind6.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC7 | X | X |  | 132kV | COM |  | Dummy CB Open | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC8 | X | X |  | 132kV | COM |  | Dummy CB Closed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC9 | X | X |  | 132kV | COM | LVAC Urgent | LVAC Mains No 1 MCCB Open | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC10 | X | X |  | 132kV | COM |  | LVAC Mains No 1 MCCB Closed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind10.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC11 | X | X |  | 132kV | COM | LVAC Urgent | LVAC Mains No 1 MCCB Tripped | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind11.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC12 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC12 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind12.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC13 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC13 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC14 | X | X |  | 132kV | COM |  | Spare - Slot G / Binary Input CC14 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC15 | X | X |  | 132kV | COM | LVAC Urgent | LVAC Generator MCCB Open | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot G / Binary Input CC16 | X | X |  | 132kV | COM |  | LVAC Generator MCCB Closed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO2.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO2/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC1 | X | X |  | 132kV | COM | LVAC Urgent | LVAC Generator MCCB Tripped | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC2 | X | X | X | 132kV | COM | LVAC Non Urgent | Prot Panels 230VAC Ring 1 Supply Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind2.stVal[ST] |  | 351 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC3 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC3 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind3.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC4 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC4 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC5 | X | X | X | 132kV | COM | LVAC Non Urgent | Telecom Panels 230VAC Ring Supply Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind5.stVal[ST] |  | 354 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC6 | X | X | X | 132kV | COM | LVAC Non Urgent | Prot Panels 110VAC Ring 1 Supply Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind6.stVal[ST] |  | 355 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC7 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC7 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC8 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC8 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC9 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC9 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC10 | X | X | X | 132kV | COM | LVAC Urgent | LVAC Mains No 1 Supply IED Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind10.stVal[ST] |  | 272 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC11 | X | X | X | 132kV | COM | LVAC Urgent | LVAC Generator Supply IED Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind11.stVal[ST] |  | 273 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC12 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC12 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind12.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC13 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC13 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC14 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC14 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC15 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC15 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot H / Binary Input CC16 | X | X |  | 132kV | COM |  | Spare - Slot H / Binary Input CC16 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO3.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO3/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC1 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No1 48V Battery Charger Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind1.stVal[ST] |  | 214 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC2 | X | X |  | 132kV | COM |  | No1 48V Battery Charger On Boost | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind2.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC3 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No1 48V Battery Charger Mains Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind3.stVal[ST] |  | 216 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC4 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No1 48V Battery Charger HV Shutdown | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind4.stVal[ST] |  | 217 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC5 | X | X | X | 132kV | COM | 48V Battery Charger Non Urgent | No1 48V Distribution Non Urgent | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind5.stVal[ST] |  | 218 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC6 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No1 48V Distribution Supply Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind6.stVal[ST] |  | 219 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC7 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC7 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind7.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC8 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC8 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC9 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No2 48V Battery Charger Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind9.stVal[ST] |  | 220 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC10 | X | X |  | 132kV | COM |  | No2 48V Battery Charger On Boost | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind10.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC11 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No2 48V Battery Charger Mains Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind11.stVal[ST] |  | 222 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC12 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No2 48V Battery Charger HV Shutdown | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind12.stVal[ST] |  | 223 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC13 | X | X | X | 132kV | COM | 48V Battery Charger Non Urgent | No2 48V Distribution Non Urgent | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind13.stVal[ST] |  | 224 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC14 | X | X | X | 132kV | COM | 48V Battery Charger Urgent | No2 48V Distribution Supply Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind14.stVal[ST] |  | 225 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC15 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC15 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC16 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC16 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC17 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No1 110V Battery Charger Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind17.stVal[ST] |  | 228 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind17/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC18 | X | X |  | 132kV | COM |  | No1 110V Battery Charger On Boost | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind18.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind18/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC19 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No1 110V Battery Charger Mains Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind19.stVal[ST] |  | 230 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC20 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No1 110V Battery Charger HV Shutdown | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind20.stVal[ST] |  | 231 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind20/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC21 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No1 110V Battery Urgent | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind21.stVal[ST] |  | 232 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind21/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC22 | X | X | X | 132kV | COM | 110V Battery Charger Non Urgent | No1 110V Battery Non Urgent | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind22.stVal[ST] |  | 233 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind22/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC23 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC23 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind23.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind23/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC24 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC24 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind24.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind24/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC25 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No2 110V Battery Charger Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind25.stVal[ST] |  | 236 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind25/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC26 | X | X |  | 132kV | COM |  | No2 110V Battery Charger On Boost | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind26.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind26/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC27 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No2 110V Battery Charger Mains Fail | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind27.stVal[ST] |  | 238 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind27/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC28 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No2 110V Battery Charger HV Shutdown | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind28.stVal[ST] |  | 239 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind28/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC29 | X | X | X | 132kV | COM | 110V Battery Charger Urgent | No2 110V Battery Urgent | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind29.stVal[ST] |  | 240 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind29/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC30 | X | X | X | 132kV | COM | 110V Battery Charger Non Urgent | No2 110V Battery Non Urgent | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind30.stVal[ST] |  | 241 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind30/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC31 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC31 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind31.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind31/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot J / Binary Input CC32 | X | X |  | 132kV | COM |  | Spare - Slot J / Binary Input CC32 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO4.Ind32.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO4/Ind32/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC1 | X | X |  | 132kV | COM |  | Standby Diesel Generator Running | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind1.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC2 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Watchdog | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind2.stVal[ST] |  | 245 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC3 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Engine Heater Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind3.stVal[ST] |  | 246 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC4 | X | X |  | 132kV | COM |  | Standby Diesel Generator In Auto | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind4.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC5 | X | X | X | 132kV | COM | Generator Non Urgent | Standby Diesel Generator Not In Auto | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind5.stVal[ST] |  | 248 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC6 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Low Water Level | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind6.stVal[ST] |  | 249 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC7 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Battery Charger Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind7.stVal[ST] |  | 250 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC8 | X | X |  | 132kV | COM |  | Standby Diesel Generator Load Bank CB Status | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC9 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Load Bank CB Tripped | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind9.stVal[ST] |  | 252 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC10 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator CB To Site Load Tripped | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind10.stVal[ST] |  | 253 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC11 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Earth Fault Protection Operated | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind11.stVal[ST] |  | 254 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC12 | X | X | X | 132kV | COM | Generator Urgent | Standby Diesel Generator Cumulative Alarm | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind12.stVal[ST] |  | 255 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC13 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC13 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC14 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC14 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC15 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC15 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC16 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC16 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC17 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC17 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind17.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind17/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC18 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC18 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind18.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind18/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC19 | X | X |  | 132kV | COM |  | Spare - Slot 2H / Binary Input CC19 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind19.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC20 | X | X |  | 132kV | COM |  | Spare - Slot 2H / Binary Input CC20 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind20.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind20/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC21 | X | X |  | 132kV | COM |  | Spare - Slot 2H / Binary Input CC21 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind21.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind21/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC22 | X | X | X | 132kV | COM | Fire System Urgent | Fire Protection System Defective | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind22.stVal[ST] |  | 265 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind22/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC23 | X | X | X | 132kV | COM | Fire System Urgent | Fire Protection System Disabled | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind23.stVal[ST] |  | 337 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind23/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC24 | X | X | X | 132kV | COM | Fire System Urgent | Fire Protection System Operated | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind24.stVal[ST] |  | 338 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind24/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC25 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC25 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind25.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind25/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC26 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC26 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind26.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind26/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC27 | X | X | X | 132kV | COM | Control System Urgent | Common BCU DC Supply 1 MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind27.stVal[ST] |  | 275 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind27/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC28 | X | X | X | 132kV | COM | Control System Urgent | Common BCU DC Supply 2 MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind28.stVal[ST] |  | 276 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind28/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC29 | X | X | X | 132kV | COM | Control System Urgent | Common BCU DC Alarm/Indication MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind29.stVal[ST] |  | 277 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind29/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC30 | X | X | X | 132kV | COM | Control System Urgent | Common BCU DC Control MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind30.stVal[ST] |  | 278 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind30/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC31 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC31 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind31.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind31/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2H/ Binary Input CC32 | X | X |  | 132kV | COM |  | Spare - Slot 2H/ Binary Input CC32 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO5.Ind32.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO5/Ind32/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC1 | X | X | X | 132kV | COM | Control System Urgent | GPS Clock 1 Time Sync Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind1.stVal[ST] |  | 281 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind1/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC2 | X | X | X | 132kV | COM | Control System Urgent | GPS Clock 1 DC Supply 1 /2MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind2.stVal[ST] |  | 282 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind2/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC3 | X | X | X | 132kV | COM | Control System Urgent | COM Red LAN Switch Failed | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind3.stVal[ST] |  | 283 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind3/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC4 | X | X | X | 132kV | COM | Control System Urgent | COM Red LAN DC Supply 1/2 MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind4.stVal[ST] |  | 284 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind4/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC5 | X | X |  | 132kV | COM |  | 110V AC Lighting MCB Trip | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind5.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind5/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC6 | X | X | X | 132kV | COM | Control System Urgent | Bay 01 BCU Main PSU Not Ready | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind6.stVal[ST] |  | 286 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind6/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC7 | X | X | X | 132kV | COM | Control System Urgent | Bay 01 BCU Backup PSU Not Ready | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind7.stVal[ST] |  | 287 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind7/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC8 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC8 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind8.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind8/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC9 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC9 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind9.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind9/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC10 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC10 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind10.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind10/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC11 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC11 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind11.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind11/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC12 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC12 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind12.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind12/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC13 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC13 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind13.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind13/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC14 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC14 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind14.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind14/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC15 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC15 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind15.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind15/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | Common Alarm | Slot 2J/ Binary Input CC16 | X | X |  | 132kV | COM |  | Spare - Slot 2J/ Binary Input CC16 | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/GGIO6.Ind16.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/GGIO6/Ind16/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Indication | BCU Alarm | BCU Dummy Open | X | X | X | 132kV | COM | Indication | Dummy CB Open | REM_POS_SWG | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind22.stVal[ST] |  | 313 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind22/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Indication | BCU Alarm | BCU Dummy Closed | X | X | X | 132kV | COM | Indication | Dummy CB Closed | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind23.stVal[ST] |  | 314 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind23/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | BCU Health Status Failed | X | X | X | 132kV | COM | Control System Urgent | BCU Fail | REM_ALM_ON_OFF | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind29.stVal[ST] |  | 328 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind29/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | BCU Health Status Not Normal | X | X | X | 132kV | COM | Control System Urgent | BCU Health Status Not Normal | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind28.stVal[ST] |  | 329 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind28/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | BCU Restarted | X | X |  | 132kV | COM |  | BCU Restarted | REM_NOT_REQUIRED | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind27.stVal[ST] |  |  | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind27/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | BCU On Local | X | X | X | 132kV | COM | Control System Urgent | BCU On Local | REM_ALM_REM_LOC | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind49.stVal[ST] |  | 330 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind49/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | BCU Controls Disabled | X | X | X | 132kV | COM | Control System Urgent | BCU Controls Disabled | REM_ALM_OFF_ON | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind48.stVal[ST] |  | 331 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind48/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | Red LAN Alarm | X | X | X | 132kV | COM | Control System Urgent | BCU Red LAN Alarm | REM_ALM_NOR_ALM | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind19.stVal[ST] |  | 332 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind19/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | Black LAN Alarm | X | X | X | 132kV | COM | Control System Urgent | BCU Black LAN Alarm | REM_ALM_NOR_ALM | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind20.stVal[ST] |  | 333 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind20/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Alarm | BCU Alarm | Internal Clock Faulty | X | X | X | 132kV | COM | Control System Urgent | Clock Synchronisation Alarm | REM_ALM_NOR_ALM | COM |  | BOOL |  | BOOL | CON/eveGGIO1.Ind21.stVal[ST] |  | 334 | 1 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/eveGGIO1/Ind21/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Control | BCU Control | BCU Dummy Open | X | X | X | 132kV | COM | Control | Dummy CB Open | REM_CMD_SWG | COM |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO42.Oper.ctlVal[CO] |  | 212 | 12 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/vinGGIO1/SPCSO42/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Control | BCU Control | BCU Dummy Close | X | X | X | 132kV | COM | Control | Dummy CB Close | REM_CMD_SWG | COM |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO43.Oper.ctlVal[CO] |  | 213 | 12 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/vinGGIO1/SPCSO43/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Control | Control | Standby Diesel Generator Start | X | X | X | 132kV | COM | Control | Standby Diesel Generator Start | REM_CMD_START | COM |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO44.Oper.ctlVal[CO] |  | 219 | 12 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/vinGGIO1/SPCSO44/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Control | Control | Standby Diesel Generator Stop | X | X | X | 132kV | COM | Control | Standby Diesel Generator Stop | REM_CMD_STOP | COM |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO45.Oper.ctlVal[CO] |  | 220 | 12 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/vinGGIO1/SPCSO45/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | Common | COM | COM |  | C650 | 192.168.248.20 /23 | BCU | LIMKECOMBCU01 | Control | Control | Standby Diesel Generator Enable % Load | X | X | X | 132kV | COM | Control | Standby Diesel Generator Enable % Load | REM_CMD_OUT_IN | COM |  | BOOL |  | BOOL | CON/vinGGIO1.SPCSO46.Oper.ctlVal[CO] |  | 221 | 12 | [5 empty] | LIMKECOMBCU01!LIMKECOMBCU01CON/vinGGIO1/SPCSO46/Oper.ctlVal[CO]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Frequency | X | X | X | 132 kV | LVAC |  | Frequency | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.Hz.mag.f[MX] |  | 0 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/Hz/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Phase R-Y Voltage | X | X | X | 132 kV | LVAC |  | Phase R-Y Voltage | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PPV.phsAB.cVal.mag.f[MX] |  | 1 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/PPV.phsAB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Phase Y-B Voltage | X | X | X | 132 kV | LVAC |  | Phase Y-B Voltage | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PPV.phsBC.cVal.mag.f[MX] |  | 2 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/PPV.phsBC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Phase B-R Voltage | X | X | X | 132 kV | LVAC |  | Phase B-R Voltage | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PPV.phsCA.cVal.mag.f[MX] |  | 3 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/PPV.phsCA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Incoming R-N | X | X | X | 132 kV | LVAC |  | Incoming R-N | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PhV.phsA.cVal.ang.f[MX] |  | 4 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/PhV.phsA/cVal.ang.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Incoming Y-N | X | X | X | 132 kV | LVAC |  | Incoming Y-N | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PhV.phsB.cVal.mag.f[MX] |  | 5 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/PhV.phsB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Incoming B-N | X | X | X | 132 kV | LVAC |  | Incoming B-N | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PhV.phsC.cVal.mag.f[MX] |  | 6 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/PhV.phsC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Current Red | X | X | X | 132 kV | LVAC |  | Current Red | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.A1.phsA.cVal.mag.f[MX] |  | 7 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/A1.phsA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Current Yellow | X | X | X | 132 kV | LVAC |  | Current Yellow | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.A1.phsB.cVal.mag.f[MX] |  | 8 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/A1.phsB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Current Blue | X | X | X | 132 kV | LVAC |  | Current Blue | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.A1.phsC.cVal.mag.f[MX] |  | 9 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/A1.phsC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | Watts | X | X | X | 132 kV | LVAC |  | Watts | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.TotW.mag.f[MX] |  | 10 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/TotW/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Analog | LVAC Measurements INC01 | VAr | X | X | X | 132 kV | LVAC |  | VAr | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.TotVAr.mag.f[MX] |  | 11 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Measurements/PriFouMMXU1/TotVAr/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC System Alarms INC01 | LVAC Protection Clock Synchronisation Alarm | X | X | X | 132 kV | LVAC | LVAC Supplies Urgent | LVAC Protection Clock Synchronisation Alarm | REM_ALM_ON_OFF | LVAC |  | BOOL |  | BOOL | System/LLN0.SyncSt.stVal[ST] |  | 0 | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01System/LLN0/SyncSt/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Event | LVAC Voltage Protection Alarms INC01 | LVAC Overvoltage Protection Start | X | X |  | 132 kV | LVAC |  | LVAC Overvoltage Protection Start | REM_CEL_RST_START | LVAC |  | BOOL |  | BOOL | Protection/VtpPhsPTOV1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/VtpPhsPTOV1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Voltage Protection Alarms INC01 | LVAC Overvoltage Protection Operated | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Overvoltage Protection Operated | REM_ALM_RST_OPTD | LVAC |  | BOOL |  | BOOL | Protection/VtpPhsPTOV1.Op.general[ST] |  | 1 | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/VtpPhsPTOV1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Voltage Protection Alarms INC01 | LVAC Overvoltage Protection Disabled | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Overvoltage Protection Disabled | REM_ALM_IN_OUT_15 | LVAC |  | ENUM |  | USINT | Protection/VtpPhsPTOV1.Beh.stVal[ST] |  | 12 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/VtpPhsPTOV1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Event | LVAC Voltage Protection Alarms INC01 | LVAC Undervoltage Protection Start | X | X |  | 132 kV | LVAC |  | LVAC Undervoltage Protection Start | REM_CEL_RST_START | LVAC |  | BOOL |  | BOOL | Protection/VtpPhsPTUV1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/VtpPhsPTUV1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Voltage Protection Alarms INC01 | LVAC Undervoltage Protection Operated | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Undervoltage Protection Operated | REM_ALM_RST_OPTD | LVAC |  | BOOL |  | BOOL | Protection/VtpPhsPTUV1.Op.general[ST] |  | 2 | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/VtpPhsPTUV1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Voltage Protection Alarms INC01 | LVAC Undervoltage Protection Disabled | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Undervoltage Protection Disabled | REM_ALM_IN_OUT_15 | LVAC |  | ENUM |  | USINT | Protection/VtpPhsPTUV1.Beh.stVal[ST] |  | 13 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/VtpPhsPTUV1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Event | LVAC Frequency Protection Alarms INC01 | LVAC Over Frequency Protection Start | X | X |  | 132 kV | LVAC |  | LVAC Over Frequency Protection Start | REM_CEL_RST_START | LVAC |  | BOOL |  | BOOL | Protection/FrqPTOF1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/FrqPTOF1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Frequency Protection Alarms INC01 | LVAC Over Frequency Protection Operated | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Over Frequency Protection Operated | REM_ALM_RST_OPTD | LVAC |  | BOOL |  | BOOL | Protection/FrqPTOF1.Op.general[ST] |  | 3 | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/FrqPTOF1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Frequency Protection Alarms INC01 | LVAC Over Frequency Protection Disabled | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Over Frequency Protection Disabled | REM_ALM_IN_OUT_15 | LVAC |  | ENUM |  | USINT | Protection/FrqPTOF1.Beh.stVal[ST] |  | 14 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/FrqPTOF1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Event | LVAC Frequency Protection Alarms INC01 | LVAC Under Frequency Protection Start | X | X |  | 132 kV | LVAC |  | LVAC Under Frequency Protection Start | REM_CEL_RST_START | LVAC |  | BOOL |  | BOOL | Protection/FrqPTUF1.Str.general[ST] |  |  | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/FrqPTUF1/Str/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Frequency Protection Alarms INC01 | LVAC Under Frequency Protection Operated | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Under Frequency Protection Operated | REM_ALM_RST_OPTD | LVAC |  | BOOL |  | BOOL | Protection/FrqPTUF1.Op.general[ST] |  | 4 | 1 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/FrqPTUF1/Op/general[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.21 /23 | P141_LVAC | LIMKELVACINC01 | Alarm | LVAC Frequency Protection Alarms INC01 | LVAC Under Frequency Protection Disabled | X | X | X | 132 kV | LVAC | LVAC Supplies Non-Urgent | LVAC Under Frequency Protection Disabled | REM_ALM_IN_OUT_15 | LVAC |  | ENUM |  | USINT | Protection/FrqPTUF1.Beh.stVal[ST] |  | 15 | 30 | [5 empty] | LIMKELVACINC01!LIMKELVACINC01Protection/FrqPTUF1/Beh/stVal[ST]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Frequency | X | X | X | 132 kV | LVAC |  | Frequency | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.Hz.mag.f[MX] |  | 0 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/Hz/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Phase R-Y Voltage | X | X | X | 132 kV | LVAC |  | Phase R-Y Voltage | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PPV.phsAB.cVal.mag.f[MX] |  | 1 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/PPV.phsAB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Phase Y-B Voltage | X | X | X | 132 kV | LVAC |  | Phase Y-B Voltage | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PPV.phsBC.cVal.mag.f[MX] |  | 2 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/PPV.phsBC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Phase B-R Voltage | X | X | X | 132 kV | LVAC |  | Phase B-R Voltage | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PPV.phsCA.cVal.mag.f[MX] |  | 3 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/PPV.phsCA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Incoming R-N | X | X | X | 132 kV | LVAC |  | Incoming R-N | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PhV.phsA.cVal.ang.f[MX] |  | 4 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/PhV.phsA/cVal.ang.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Incoming Y-N | X | X | X | 132 kV | LVAC |  | Incoming Y-N | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PhV.phsB.cVal.mag.f[MX] |  | 5 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/PhV.phsB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Incoming B-N | X | X | X | 132 kV | LVAC |  | Incoming B-N | REM_NOT_REQUIRED | LVAC |  | VECTOR |  | REAL | Measurements/PriFouMMXU1.PhV.phsC.cVal.mag.f[MX] |  | 6 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/PhV.phsC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Current Red | X | X | X | 132 kV | LVAC |  | Current Red | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.A1.phsA.cVal.mag.f[MX] |  | 7 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/A1.phsA/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Current Yellow | X | X | X | 132 kV | LVAC |  | Current Yellow | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.A1.phsB.cVal.mag.f[MX] |  | 8 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/A1.phsB/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Current Blue | X | X | X | 132 kV | LVAC |  | Current Blue | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.A1.phsC.cVal.mag.f[MX] |  | 9 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/A1.phsC/cVal.mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | Watts | X | X | X | 132 kV | LVAC |  | Watts | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.TotW.mag.f[MX] |  | 10 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/TotW/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Analog | LVAC Measurements GEN01 | VAr | X | X | X | 132 kV | LVAC |  | VAr | REM_NOT_REQUIRED | LVAC |  | FLOAT |  | REAL | Measurements/PriFouMMXU1.TotVAr.mag.f[MX] |  | 11 | 30 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01Measurements/PriFouMMXU1/TotVAr/mag.f[MX]
| Limekiln 132kV Substation | LIMK | E | LVAC | LVAC | LVAC |  | P141 | 192.168.248.22 /23 | P141_LVAC1 | LIMKELVACGEN01 | Alarm | LVAC System Alarms GEN01 | LVAC Protection Clock Synchronisation Alarm | X | X | X | 132 kV | LVAC | LVAC Supplies Urgent | LVAC Protection Clock Synchronisation Alarm | REM_ALM_ON_OFF | LVAC |  | BOOL |  | BOOL | System/LLN0.SyncSt.stVal[ST] |  | 0 | 1 | [5 empty] | LIMKELVACGEN01!LIMKELVACGEN01System/LLN0/SyncSt/stVal[ST]
_End
Note on AM1: RTSD: The Copdata Variable Name is to be configured to contain the operating voltage of 400kV, despite the interim operating voltage of 275kV, this is to reduce future rework during the future 400kV upgrade, N.B. this does not apply to the HMI Presentation Text (see comments on the relevant column)